Smart-UPS

Rack Mount Supplement

English

American Power Conversion

American Power Conversion  132 Fairgrounds Road

West Kingston, Rhode Island  02892  Phone (401) 789-5735

Part Number: 990-7021A  Revision: 3 Date: 9/24/96  Approved: sjm

Note: Specifications contained herein are subject to change without notice.

Copyright © 1996 American Power Conversion. All rights reserved.

1. Introduction

2. Presentation

3. Installation

4. Options

5. Battery Replacement

6. Specifications

7. How to Determine On-battery Run Time

1.	Introduction

This supplement covers differences between the rack mount and stand alone versions of the UPS. Please refer to the User€s Manual for basic information about the UPS.

2.	Presentation

Rear Panel, 700, 1000, 1400 VA

100/120 VAC

230 VAC

Rear Panel, 2200, 3000 VA

100/120 VAC

230 VAC

3.	Installation Tips

Please observe the following items when installing the UPS.

¬	The UPS comes with standard 19" (46.5 cm) rack mount brackets installed. An accessory set of 23" (59.2 cm) brackets are available for the 700, 1000, and 1400 VA models. Contact your dealer or the factory at the number in the front of this manual for more information.

¬	The 2200 and 3000 VA models of the UPS are supplied with L-channel supports. These supports may be used with these models to ease installation. The L-channel supports are available as an accessory for the 700, 1000, and 1400 VA models. Contact your dealer or the factory at the number in the front of this manual for more information.

¬	Caution: The 2200 and 3000 VA models require two or more people to install due to their weight.

¬	The UPS is not supplied with screws to attach the mounting brackets (ears) to the rack, as the size of screw varies according to the type of rack used.

¬	UPSs are heavy. Select a rack location sturdy enough to handle the weight. Try to mount the UPS near the bottom of the rack.

¬	Select a rack location with adequate air flow that is free from excessive dust. Ensure that the air vents on the sides of the UPS are not blocked. Do not operate the UPS where temperature or humidity are outside the limits in Section 12 of the User€s Manual.

¬	Caution: Remove the UPS before transporting the rack.

¬	Two additional sets of bracket holes are located on the sides of the UPS (see below). These holes allow mounting the brackets with a three inch or six inch setback. Move the mounting brackets back if desired to optimize the esthetic or physical requirements of the rack.

Caution: Check the rack to make sure it won€t tip after moving the mounting brackets.

Installing the Support Brackets

1.	Verify the contents of the kit. It contains: two adjustable-length L-channel supports, eight clip nuts, eight 10-32 x 1/2€ flat-head screws, and eight washers. The washers are for use with square rack holes only.

2.	If the rack uses threaded holes, drill out the appropriate front rail rack holes with a 7/32€ drill bit. This step is not required when mounting in racks with square holes.

3.	Install clip nuts on the uppermost and lowermost holes at each end of the L-channel supports. Orient the clip nut as shown in the drawing above (3). The nuts should be to the inside of the cabinet when the supports are installed.

4.	Secure the front of the support to the front cabinet rack using two 10-32 x 1/2 flat-head screws (4). Note that the front ear of the L-channel support has a square cutout on the mounting ear (1), and the rear ear has no cutout (2). For cabinets with square rack holes, use a washer under the head of each screw.

5.	Loosen the two 10-32 x 5/16 pan-head screws that lock together the two halves of the L-channel support (5). Slide the outer half of the support to the rear until it contacts the rear rack of the cabinet. If the rack uses threaded holes, drill out the appropriate rear rail rack holes with a 7/32 drill bit (see Step 3). Secure the rear of the support to the rear cabinet rack using two 10-32 x 1/2 flat-head screws. For cabinets with square rack holes, use a washer under the head of each screw.

6.	Securely tighten the two 10-32 x 5/16 pan-head screws that lock together the halves of the L-channel support (5).

7.	Repeat steps 3 through 6 to install the other L-channel support.

8.	Slide the UPS onto the L-channel supports and use rack hardware to secure the UPS mounting ears to the rack rails.

4.	Options

Accessory receptacle plates are available for the 2200 VA and 3000 VA models. These plates offer different receptacle configurations and hard wire installation. Contact your dealer or the factory at the number in the front of this manual for more information.

5.	Battery Replacement

Battery replacement is a safe procedure, isolated from electrical hazards. You may leave the UPS and the loads on for the following procedure.

700, 1000, 1400 VA

1.	Reach into the finger pull and open the front cover. Swing the cover open as shown.

2.	Unhook the side of the cover from the chassis and lift it away to expose the battery door.

3.	Use a flat-blade or Phillips screwdriver or a coin to remove the two battery door screws and open the door.

4.	Grasp the tab and gently pull the battery out of the UPS. Note: Be careful removing the batteries  they are heavy.

5.	Disconnect the battery leads. Loosen the connectors by gently wiggling them while pulling straight back from the battery connector.

6.	Connect the battery leads to the new battery. Connect the red wire to the positive (+) terminal and the black wire to the negative () terminal. Note: Small sparks at the battery connectors are normal during battery connection.

Now slide the battery into the UPS, close the battery door, replace the battery compartment screws, and replace the front cover.

7.	Dispose of the battery properly at an appropriate recycling facility or return it to the supplier in the packing material for the new battery. See the instructions supplied with the new battery for more information.

2200, 3000 VA

1.	Reach into the finger pull and open the front cover. Swing the cover open as shown.

2.	Unhook the side of the cover from the chassis and lift it away to expose the battery door.

3.	Use a flat-blade or phillips screwdriver or a coin to remove the three battery door screws and open the door.

4.	Grip the wires for the front set of batteries and pull firmly to disconnect the wires. Remove the batteries. Set aside the foam spacer located between the batteries. Now reach into the battery compartment and grasp either the white cord (if it is present), or the wires for the other set of batteries. Again, pull firmly to disconnect the wires. Remove the second set of batteries. Note: Be careful removing the batteries  they are heavy.

5.	Slide the first set of new batteries into the unit. Hold the connector down below the top of the batteries and toward the door; otherwise the assembly will not fit. Guide the connector over the top of the batteries and connect it to the rear connector of the battery compartment. Set the foam spacer against the rear batteries to prevent the wires from being pinched. Slide the second set of batteries in, then guide the connector over the batteries and connect it to the front connector of the battery compartment. Note: Small sparks at the battery connectors are normal during battery connection. Close the battery compartment door, making sure that no wires are pinched. Replace the battery compartment screws and replace the front cover.

6.	Dispose of the battery properly at an appropriate recycling facility or return it to the supplier in the packing material for the new battery. See the instructions supplied with the new battery for more information.

6.	Specifications

| Model | Size (H x W x D) | Net Weight (shipping) |
| --- | --- | --- |
| SU700RM |  | 18.2 (20.9) kg 40 (46) lb. |
| SU1000RM | 13 x 48.3 x 38.1 cm 5.22 x 19 x 15 inches | 20.8 (23.5) kg 46 (52) lb. |
| SU1400RM |  | 25 (27.6) kg 55 (61) lb. |
| SU2200RM |  | 54.5 (61.7) kg 120 (136) lb. |
| SU2200RMXL | 22.2 x 48.3 x 50.8 cm 8.72 x 19 x 20 inches | 58.5 (65.8) kg 129 (145) lb. |
| SU2200RMXLI |  | 61 (68) kg 134 (150) lb. |
| SU3000RM |  | 58.5 (65.8) kg 129 (145) lb. |

7.	How to Determine On-battery Run Time

This table will aid in estimating the length of run time that you may expect for a given load.

1.	To calculate the on-battery run time, first determine the total load protected by the UPS in Volt-Amps. Obtain load figures from either the labelling on the protected equipment or the accompanying literature. For loads specified in watts, multiply the specified figure by 1.4. For loads specified in amps, multiply the specified figure by the line voltage.

2.	Add the individual loads to determine the total load.

3.	Compare the total load of the system to the run time table below.

Typical On-battery Run Time Versus Load, in Minutes

SU700RM	SU1000RM	SU1400RM	SU2200RM	SU3000RM

50 VA		140		150		192		366		297

75 VA		113		125		152		309		258

100 VA		85		100		125		268		228

150 VA		55		75		90		209		183

200 VA		38		58		69		170		152

250 VA		26		44		54		142		128

300 VA		20		36		44		121		110

350 VA		17		28		36		104		96

400 VA		14		24		30		91		84

450 VA		11		20		25		80		75

500 VA		9		18		22		71		67

550 VA		7		15		19		64		60

600 VA		6		13		16		57		54

700 VA		5		11		13		46		44

800 VA		-		9		11		38		36

900 VA		-		7		9		32		31

1000 VA		-		6		8		27		26

1200 VA		-		-		6		21		20

1400 VA		-		-		5		17		16

1600 VA		-		-		-		14		13

2000 VA		-		-		-		10		10

2200 VA		-		-		-		8		8

2500 VA		-		-		-		-		7

3000 VA		-		-		-		-		5